{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":21,"n_cols":6,"rows_kept":21,"merged":[[0,0,0,5],[2,0,2,1],[7,0,7,1],[13,0,13,1],[20,0,20,5],[21,0,21,5]],"flags":["formulas_cached_only"]}
["视频监控系统规格参数"]
["序列","设备名称","技术参数","数量","单位","备注"]
["1.前端部分"]
[1,"网络筒型摄像机","1、图像最大分辨率不低于2560x1440\n2、★信噪比不小于55dB。（公安部检验报告证明）\n3、★支持红外补光、白光补光，有效补光距离均能达到30m（公安部检验报告证明）\n4、需支持IP66防尘防水。\n5、支持DC12V或poe供电\n6、内置1个麦克风，1个RJ45网络接口\n7、靶面尺寸为1/2.7英寸",14,"台"]
[2,"网络半球摄像机","1、★在2560x1440下分辨力可达到1400TVL（公安部检验报告证明）\n2、★靶面尺寸为1/2.7英寸（公安部检验报告证明）\n3、需支持IP66防尘防水。\n4、支持DC12V或poe供电\n5、内置1个麦克风，1个RJ45网络接口\n6、信噪比不小于55dB。",2,"台"]
[3,"防水箱",null,1,"个"]
[4,"支架","材质: 铝合金",16,"个"]
["2.传输部分"]
[1,"电源线","2*1.0",100,"米"]
[2,"网线","6类非屏蔽",400,"米"]
[3,"POE交换机","1、提供8个千兆PoE电口\n2、交换容量：16 Gbps\n3、包转发率：11.91 Mpps\n4、配置：可用千兆PoE电接口数量≥8\n5、提供CQC认证证书\n6、支持自适应802.3af/at供电标准，整机最大输出功率≥65 W\n7、支持6KV防浪涌（PoE口）\n",1,"个"]
[4,"线管",null,100,"米"]
[5,"线槽",null,20,"米"]
["3.机房设备"]
[1,"监控硬盘","8T，SATA，7200rpm，256MB缓存",1,"块"]
[2,"机柜","1米",1,"个"]
[3,"显示器","27寸",0,"个"]
[4,"录像机","1、具有1个HDMI接口、1个VGA接口、2个千兆以太网口、3个USB2.0接口（其中2个为前置）、内置4个SATA硬盘接口；1路RCA音频输入接口、1路RCA音频输出接口；16路报警输入接口、4路报警输出接口。\n2、可接入1T、2T、3T、4T、6T、8T、10T容量的SATA接口硬盘；\n3、最大接入路数：32路。满负载条件下的最大接入带宽160Mbps、最大存储带宽128Mbps、最大转发带宽128Mbps。\n4、★支持开启SVC解码功能，可同时回放5路400W分辨率、H.264/H.265编码格式的视频图像，解码总资源为10个1920×1080格式的视频图像。（公安部检验报告证明）\n5、★显示输出分辨率具有1024×768/60Hz、1280×720/60Hz、1280×1024/60Hz、1600×1200/60Hz、1920×1080/60Hz、2560×1440/60Hz、4K(3840×2160)/30Hz、4K(4096×2160)/30Hz设置选项。（公安部检验报告证明）\n6、可同时显示输出10路H.265/H.264编码、25fps、1920×1080格式的视频图像。 \n7、接入警戒摄像机，支持对IPC的声音和闪光参数进行配置， 支持通过移动侦测、区域入侵、越界侦测、进入区域和离开区域事件联动一个或多个IPC的声光报警，可以对声光联动一键撤防。",1,"台"]
[5,"耗材","水晶头  插排",1,"批"]
[6,"施工费",null,1,"批"]
["1、标星号为必须满足项 ,一项不满足废标。非标星号项，3项以及以上不满足，废标处理。"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}